SECTION 28 13 26.03

ACCESS CONTROL REMOTE DEVICES

PART 2 - PRODUCTS

2.01	General

- The family of intelligent controllers and peripheral interface devices must provide an open architecture family of products that enables a choice of host software system vendor without replacement of hardware.

- The Linux based intelligent controller must provide decision making, event reporting, and database storage as a hardware platform.  Two reader interfaces must provide control for one door and capable of supporting up to an additional 16 doors paired and or alternate reader configurations with peripheral interface devices.

- The controller must communicate with the host via on-board 10BaseT/100BaseTX Ethernet port and support TLS encryption as a minimum security implementation.

- The intelligent controller must be capable of elaborate processes and procedures without host intervention. Once configured, the intelligent controller must function independently of the host, and must be capable of controlling access, managing alarms, interfacing with an array of hardware devices, all while providing the decision-making oversight that each system configuration requires.

- The intelligent controller must provide centralized biometric template management and support a wide range of reader technologies, including OSDP, Wiegand, magnetic stripe and biometric.

- One physical barrier must be controlled.  Each reader port must accommodate a read head that utilizes OSDP (RS-485), OSDP SC, Wiegand, magnetic stripe, or F2F protocol/electrical signaling, one or two wire LED controls, and buzzer control.  One reader port will also accommodate two-wire RS-485 electrical signaling standards.

- Controller must support, as a minimum the following open standards, PSIA Area Control, SNMPv3/v2c, OSDP and OSDP SC.

- The controller must utilize a cryptographic module, like OpenSSL FIPS Object Module RE, that is validated to FIPS 140-2 thus providing a certified implementation of TLS.

2.01	Technical Specifications

- The interface is for use in low voltage, Class 2 circuits only.

- The installation of this device must comply with all local fire and electrical codes.

- Power Input

- PoE (12.95 W), compliant to IEEE 802.3af or

- PoE+ (25 W), compliant to IEEE 802.3at or

- 12 Vdc +/- 10%, 1.8A maximum

- Power Output

- PoE: 12 Vdc @ 625 mA including reader and Auxiliary Power output *

- PoE+ or external 12 Vdc: 12 Vdc @ 1.25 A including reader and Auxiliary Power output *

- * Excluding micro USB port

- Micro USB Port: 5 Vdc maximum (deduct 270 mA from reader and Auxiliary Power output)

- SRAM Backup Battery: Rechargeable battery

- Host Communication:	Ethernet: 10-BaseT/100Base-TX

- Inputs:

  - Two unsupervised/supervised, Programmable End of Line resistors, 1k/1k ohm, 1 %, ¼ watt standard

  - One unsupervised input dedicated for cabinet tamper

- Outputs:	Two relays: Form-C contacts: 2 A @ 30 Vdc, resistive

- Reader Interface

  - Power: 12 Vdc ± 10 %: PoE, PoE+ or local power supply, 300 mA maximum

  - Data Inputs

    - Reader port 1: TTL compatible, F/2F or 2-wire RS-485

    - Reader port 2: TTL compatible or F/2F

  - LED Output:	TTL compatible, high > 3 V, low < 0.5 V, 5 mA source/sink maximum

  - Buzzer Output:	Open collector, 12 Vdc open circuit maximum, 40 mA sink maximum

- Cable Requirements

  - Power:	1 twisted pair, 18 AWG (when using local 12 Vdc power supply)

  - Ethernet:	CAT-5, minimum

  - Reader data (TTL):	6-conductor, 18 AWG, 500 ft. (152 m) maximum

  - Reader data (F/2F):	4-conductor, 18 AWG, 500 ft. (152 m) maximum

  - Reader data (RS-485):	1 twisted pair, shielded.  24 AWG, 120 ohm impedance, 2000 ft. (610 m) maximum

  - Alarm Input:	1 twisted pair per input, 30 ohm maximum

  - Outputs:	As required for the load

- Environmental

  - Temperature:

    - Storage	-55 to +85 °C

    - Operating	0 to +70 °C

  - Humidity:	5 to 95 % RHNC

- Mechanical

  - Dimension:

    - 5.5 in. (140 mm) W x 2.75 in. (70 mm) L x 0.96 in. (24 mm) H without bracket

    - 5.5 in. (140 mm) W x 3.63 in. (92 mm) L x 1.33 in. (34 mm) H with bracket

  - Weight

    - 3.6 oz. (103 g) without bracket

    - 4.43 oz. (125.5 g) with bracket

- Product Compliance:

- UL294 Recognized. Note:  For UL, the Power Sourcing Equipment (PSE) such as a PoE or PoE+ enabled network switch. and/or PoE or PoE+ power injectors must be UL Listed under UL294B.

- FCC Part 15 Class A

- CE Compliant

- RoHS (2011/65/EU & 2015/863)

- EU REACH (1907/2006)

- California Proposition 65

- NIST Certified Encryption

- Warranty: Mercury Security warrants the product is free from defects in material and workmanship under normal use and service with proper maintenance for one year from the date of factory shipment.

2.02	Technical Features

- Connectivity: Primary Port: 10/100 Ethernet

- Security:

  - Host/Controller connection protected by TLS 1.2/1.1 or AES-256-128

  - Controller/IO Expansion connection protected by AES

  - Generate and load custom peer certificates for TLS

  - Port based network access control using 802.1X

  - Crypto memory chip

  - FIPS 140-2 user of OpenSSL

  - HTTPS protection for installer web pages

  - Secure cookies

  - SNMPv3/v2c

  - DIP switch toggle sets 5 minute time to disable webpage access

  - Disable default login credentials

  - Authorized IP address filtering

  - IP Client Proxy

  - Bulk erase controller and periphery devices during replacement

  - Strong password enforcement

- Door Control: One physical barrier can be controlled using single or paired readers.

  - Two-reader ports:12VDC regulated power, 150mA maximum

    - Port 1: clock/data, data-1/data-0, F2F or 2-wire RS-485 (2 devices)

    - Port 2: clock/data, data-1/data-0 or F2F

  - Two (2) programmable inputs, Two (2) relays, diagnostic LEDs

- Access Control:

  - 240,000 Cardholder capacity

  - 50,000 Transaction buffer

  - If/Then Macro capability

  - Adjustable Cardholder Capacity

  - Supports up to 130 inputs and 130 outputs

- Card Formats:

  - 16 card formats per active reader, 8 per offline reader

  - Entire card number reported on invalid read

  - 19 digit (64-bit) User ID and 15 digit PIN numbers maximum

  - PIV, CAC, TWIC card compatible

  - 255 Access Levels per cardholder

  - Activation/Deactivation Date or Date & Times

- Card Reader Functions

  - Multiple card format support by reader

  - Paired reader support

  - Alternate reader support

  - Elevator support

  - Turnstile support

  - Biometric device support

  - Open Supervised Device Protocol (OSDP) and OSDP SC compliant

  - Occupancy count

  - Support of multi-occupancy rules

  - Anti-passback support

    - Area-based, reader-based, or time based

    - Nested area, hard, soft, or timed forgiveness

  - Supports host-based approval rules

  - Keypad support with programmable user commands, card input

  - Shunt relay support

  - Strike follower relay support

  - Threat level and Operating Modes

  - Host controlled OSDP reader passthrough

  - Elevator floor override

- Database Functions

  - Encrypted database

  - Configurable card database

  - Supports up to nineteen (19) digital card numbers

  - Supports pin codes up to fifteen (15) digits

  - Programmable card activation and deactivation times and dates

  - Card issue code up to 32 bits, ADA and VIP flags; PIV (75 bits); Smart Card (200 bits)

  - Ability to track people and objects

- Intrusion Alarm Functions

  - Supports entry delays and exit delays

  - Area monitoring

  - Standard alarm masking

  - Provides control and alarm processing from the keypad

- Supported Integrations

  - Regional I/O shares I/O status

  - Wireless locks

  - Map Power Supply Alarms and Events using PSIA

  - Reader firmware and configuration download

  - Supports 1 total RS-485 I/O protocol

- System Functions

  - Map LifeSafety PSU alarms and events using PSIA

  - Regional IO shares IO states amongst multiple controllers

  - Relay count activations

  - Interoperability with older host software using Legacy Mode feature

  - Synchronize time using NTP

End of Section