SECTION 28 13 26.01

ACCESS CONTROL REMOTE DEVICES

PART 2 - PRODUCTS

2.01	General

- The family of intelligent controllers and peripheral interface devices must provide an open architecture family of products that enables a choice of host software system vendor without replacement of hardware.

- The Linux based intelligent controller must provide decision making, event reporting and database storage as a hardware platform. Supports up to 64 doors with peripheral interface devices.

- The intelligent controller must communicate with the host via on-board 10BaseT/100BaseTX Ethernet port and support TLS encryption as a minimum security implementation.

- The intelligent controller must be capable of elaborate processes and procedures without host intervention. Once configured, the intelligent controller must function independently of the host, and must be capable of controlling access, managing alarms, interfacing with an array of hardware devices, all while providing the decision-making oversight that each system configuration requires.

- The controller must provide a fault-tolerant host communication setup in order to efficiently manage a large network of access control panels in any system design.

- The intelligent controller must provide centralized biometric template management and support a wide range of reader technologies, including OSDP, Wiegand, magnetic stripe and biometric.

- Controller must support, as a minimum the following open standards, PSIA Area Control, SNMPv3/v2c, OSDP and OSDP SC.

- The controller must utilize a cryptographic module, like OpenSSL FIPS Object Module RE, that is validated to FIPS 140-2 thus providing a certified implementation of TLS.

2.01	Technical Specifications

- The interface is for use in low voltage, Class 2 Circuits only.

- The installation of this device must comply with all local fire and electronic codes

- Primary power: 12 to 24 Vdc ± 10%, 250 mA maximum (USB port current not included)

- Micro USB Port: 5 Vdc, 500 mA maximum (add 270 mA to primary power current)

- Memory and Clock Backup: 3 Volt Lithium, type BR2330 or CR2330

- microSD Card Format: microSD or microSDHC; 2GB to 8GB

- Host Communication: Ethernet: 10-BaseT/100Base-TX and Micro USB port (2.0) with optional adapter: pluggable model USB2-OTGE100

- Serial I/O Device Two each: 2-wire RS-485, 2,400 to 115,200 bps, asynchronous, half-duplex, 1 start bit, 8 data bits, and 1 stop bit

- Inputs: Two unsupervised dedicated for cabinet tamper and UPS fault monitoring

- Cable requirements

  - Power: 1 twisted pair, 18 AWG

  - Ethernet: CAT-5, minimum

  - RS-485: 1 twisted pair, shield, 120 ohm impedance, 24 AWG. 4,000 ft. (1,219 m) maximum cable length

- Environmental

  - Temperature: -55 to +85 °C storage, 0 to +70 °C operating

  - Humidity: 5 to 95 % RHNC

- Mechanical

  - Dimension: 5 in. (127 mm) W x 6 in. (152.4 mm) L x 1 in. (25 mm) H

  - Weight: 4.1 oz. (115 gm) nominal, board only

- Product Compliance

  - UL294 Recognized

  - FCC Part 15 Class A

  - CE Compliant

  - RoHS (2011/65/EU & 2015/863)

  - EU REACH (1907/2006)

  - California Proposition 65

  - NIST Certified Encryption

- Warranty: Mercury Security warrants the product is free from defects in material and workmanship under normal use and service with proper maintenance for one year from the date of factory shipment.

2.02	Technical Features

- Connectivity: Connectivity: 10/100 Ethernet. Optional alternate 10/100 Ethernet (using USB/Ethernet converter)

- Security:

  - Host/Controller connection protected by TLS 1.2/1.1 or AES-256/128

  - Controller/IO Expansion connection protected by AES

  - Generate and load custom peer certificates for TLS

  - Port based network access control using 802.1X

  - Crypto memory chip

  - FIPS 140-2 user of OpenSSL

  - HTTPS protection for installer web pages

  - Secure cookies

  - SNMPv3/v2c

  - DIP switch toggle sets 5 minute time to disable webpage access

  - Disable default login credentials

  - Authorized IP address filtering

  - IP Client Proxy

  - Bulk erase controller and periphery devices during replacement

  - Strong password enforcement

- Access Control:

  - 600,000 Cardholder capacity

  - 50,000 Transaction buffer

  - If/Then Macro capability

  - Adjustable cardholder capacity

  - Supports up to 1024 inputs and 1024 outputs

- Card Formats:

- 16 card formats per active reader, 8 per offline reader

- Entire card number reported on invalid read

- 19 digit (64-bit) User ID and 15 digit PIN numbers maximum

- PIV, CAC, TWIC card compatible

- 255 Access Levels per cardholder

- Activation/Deactivation Date or Date & Times

- Card Reader Functions (supported via peripheral interface devices)

- Multiple card format support by reader

- Paired reader support

- Alternate reader support

- Elevator support

- Turnstile support

- Biometric device support

- Open Supervised Device Protocol (OSDP) and OSDP SC compliant

- Occupancy count

- Support of multi-occupancy rules

- Anti-passback support

    - Area-based, reader-based, or time based

    - Nested area, hard, soft, or timed forgiveness

- Supports host-based approval rules

- Keypad support with programmable user commands, card input

- Shunt relay support

- Strike follower relay support

- Threat level and Operating Modes

- Host controlled OSDP reader passthrough

- Database Functions

- Encrypted database

- Configurable card database

- Supports up to nineteen (19) digital card numbers

- Supports pin codes up to fifteen (15) digits

- Programmable card activation and deactivation times and dates

- Card issue code up to 32 bits, ADA and VIP flags; PIV (75 bits); Smart Card (200 bits)

- Ability to track people and objects

- Intrusion Alarm Functions

- Supports entry delays and exit delays

- Area monitoring

- Standard alarm masking

- Provides control and alarm processing from the keypad

- Supported Integrations

  - Regional I/O shares I/O status

  - Wireless locks

  - Map Power Supply Alarms and Events using PSIA

  - Reader firmware and configuration download

  - Supports up to 1024 inputs and 1024 outputs

- System Functions

- Relay count activations

- Interoperability with older host software using Legacy Mode feature

- Synchronize time using NTP

End of Section