SECTION 28 13 26.05

ACCESS CONTROL REMOTE DEVICES

PART 2 - PRODUCTS

2.01	General

- The family of intelligent controllers and peripheral interface devices must provide an open architecture family of products that enables a choice of host software system vendor without replacement of hardware.

- The peripheral interface device must be a network connected, two door, PoE/PoE+ capable interface panel that provides an integrated solution when a network connection to the door is required.

- The peripheral interface device must communicate with the host via on-board 10BaseT/100BaseTX Ethernet port and support TLS encryption as a minimum security implementation.

- The reader port must be capable of supporting multi-dropped OSDP readers.

2.01	Technical Specifications

- The MR62e is for use in low voltage, Class 2 circuits only.

- Power Input

  - PoE (12.95 W), compliant to IEEE 802.3af or

  - PoE+ (25 W), compliant to IEEE 802.3at or

  - 12 Vdc +/-10 %, 1.7 A maximum

- Power Output

  - PoE: Readers and Lock, combined: 12 Vdc @ .66 A maximum

  - PoE+ or 12 Vdc: Lock 12 Vdc @ 1 A maximum, RVO, Readers 12 Vdc @ .5 A maximum

- Output: Four relays, Form-C contacts rated at 2 A @ 30 Vdc

- Inputs: Six unsupervised/supervised, End of Line resistors, 1k/1k ohm, 1%, ¼ watt standard

- Reader Interface

  - Power: 12 Vdc @ .5 A maximum

  - Communication: 2-Wire RS-485, OSDP protocol, four devices maximum

- Cable Requirements

  - Communication: Ethernet, CAT-5, minimum

  - External Input Power: 1 twisted pair, 18 AWG (if required)

  - Alarm Inputs: 1 twisted pair per input, 30 ohm maximum

  - Relay Outputs: As required for the load

  - Reader Data RS-485/power: 2 twisted pair with shield, 24 AWG, 120 ohm impedance 4000 foot (1220 m) maximum. or RS-485: 1 twisted pair with shield, 24 AWG, 120 ohm impedance, 4000 foot (1220 m) maximum and Power: 1 pair 18 AWG* * Type of cable(s) and gauge determined by length and voltage/current requirements. Local power source may be required

- Environmental

  - Temperature

    - -55 to +85 C, storage

    - 0 to +70 C, operating

  - Humidity: 5 to 95 % RHNC

- Mechanical

  - Dimension

    - 5.5 in. (140 mm) W x 2.75 in. (70 mm) L x 0.96 in. (24 mm) H without bracket

    - 5.5 in. (140 mm) W x 3.63 in. (92 mm) L x 1.33 in. (34 mm) H with bracket

  - Weight: 4 oz. (112 g) without bracket 5 oz. (142 g) with bracket

- Product Compliance

  - UL294 Recognized. For UL, the Power Sourcing Equipment (PSE) such as a PoE/PoE+ enabled network switch and/or PoE/PoE+ power injectors must be UL Listed under UL294B.

  - FCC Part 15 Class A

  - CE Compliant

  - RoHS (2011/65/EU & 2015/863)

  - EU REACH (1907/2006)

  - California Proposition 65

  - NIST Certified Encryption

- Warranty: Mercury Security warrants the product is free from defects in material and workmanship under normal use and service with proper maintenance for one year from the date of factory shipment.

2.02	Technical Features

- Connectivity: Primary Port: 10/100 Ethernet

- Security:

  - Installer web interface TLS 1.2 protected

  - Controller/IO Expansion connection protected by AES

  - Generate and load custom peer certificates for TLS

  - Port based network access control using 802.1X

  - Crypto memory chip

  - FIPS 140-2 user of OpenSSL

  - HTTPS protection for installer web pages

  - Secure cookies

  - SNMPv2c protecting all SNMP communication

  - DIP switch toggle sets 5 minute time to disable webpage access

  - Disable default login credentials

  - Authorized IP address filtering

  - Bulk erase during replacement

  - Strong password enforcement

- Door Control: Two physical barriers can be controlled using single or paired readers. Up to 4 readers supported when in paired mode.

  - One-reader port: 12VDC regulated power, 0.5A MAX all readers

  - Six (6) programmable inputs, Four (4) relays, diagnostic LEDs

- Card Formats:

  - 16 card formats per active reader, 8 per offline reader

  - Entire card number reported on invalid read

  - 19 digit (64-bit) User ID and 15 digit PIN numbers maximum

  - PIV, CAC, TWIC card compatible

- Card Reader Functions

  - Multiple card format support by reader

  - Paired reader support

  - Alternate reader support

  - Elevator support

  - Turnstile support

  - Biometric device support

  - Open Supervised Device Protocol (OSDP) and OSDP SC compliant

  - Keypad support with programmable user commands, card input

- Database Functions

  - Supports up to nineteen (19) digital card numbers

  - Supports pin codes up to fifteen (15) digits

- Intrusion Alarm Functions

  - Supports entry delays and exit delays

  - Provides control and alarm processing from the keypad

- Offline mode operation

  - Door mode: Unlocked, locked, facility code only

  - Relay Mode: Programmable for offline conditions

End of Section