SECTION 28 13 26.07

ACCESS CONTROL REMOTE DEVICES

PART 2 - PRODUCTS

2.01	General

- The family of intelligent controllers and peripheral interface devices must provide an open architecture family of products that enables a choice of host software system vendor without replacement of hardware.

- The peripheral interface device shall be used to monitor sixteen (16) inputs.

- The peripheral interface device shall be able to utilize a cryptographic module that can encrypt/decrypt communication with the intelligent controller, supporting AES encryption using a minimum 256 bit key length.

- The peripheral interface device shall utilize a crypto memory chip that provides hardened protection of secrets such keys.

2.01	Technical Specifications

- Primary Power:

- 12-24Vdc ±10%, 350mA maximum

- 12Vdc at 300mA nominal

- 24Vdc at 220mA nominal

- Communication: 2-wire RS-485, 4,000 feet using Belden 9841

- Inputs: sixteen (16) general purpose programmable type and two dedicated for tamper and power monitor

- Outputs: two (2) relays – Form-C, 5 Amp, 28Vdc

- Temperature: 0 to 70 degrees Centigrade operational, -55 to 85 degrees Centigrade storage

- Humidity: 10 to 95 percent RHNC

- Product Compliance

  - UL294 Recognized

  - FCC Part 15 Class A

  - CE Compliant

  - RoHS (2011/65/EU & 2015/863)

  - EU REACH (1907/2006)

  - California Proposition 65

- Offline mode operation

  - Relay Mode

    - Programmable for offline conditions

End of Section