SECTION 28 13 26.04

ACCESS CONTROL REMOTE DEVICES

PART 2 - PRODUCTS

2.01	General

- The family of intelligent controllers and peripheral interface devices must provide an open architecture family of products that enables a choice of host software system vendor without replacement of hardware.

- The peripheral interface device shall control one physical barrier and up to two readers (using OSDP).

- The peripheral interface device shall support a wide range of reader technologies and protocol/electrical signaling standards, including OSDP (RS-485), OSDP SC (RS-485), Wiegand (TTL), magnetic stripe, F/2F and biometric. Wiegand and magnetic strip protocols must support one or two wire LED controls, and buzzer control.

- The reader ports of the peripheral interface device shall be capable of supporting multi-dropped OSDP readers.

- The peripheral interface device shall be able to utilize a cryptographic module that can encrypt/decrypt communication with the intelligent controller, supporting AES encryption using a minimum 256 bit key length.

- The peripheral interface device shall utilize a crypto memory chip that provides hardened protection of secrets such as OSDP secure channel keys.

2.01	Technical Specifications

- The MR50-S3 is for use in low voltage, Class 2 circuits only

- The installation of this device must comply with all local fire and electrical codes.

- Primary Power: 12-24 Volts DC +/- 10%, 150mA maximum

- Intelligent Controller Communication: 2-wire RS-485 supporting 9600, 19200, 38400 or 115200 bps

- Inputs: Two unsupervised/supervised, standard EOL: 1k/1k ohm, 1%, ¼ watt, One unsupervised dedicated for cabinet tamper

- Outputs: Two relays, Form-C with dry contacts Normally open (NO) contact: 5 A @ 30 Vdc resistive, Normally closed (NC) contact: 3 A @ 30 Vdc resistive

- Reader Interface: One reader port

  - Power: 12 to 24 Vdc ± 10 % (input voltage passed through)

  - Data Inputs: TTL compatible, F/2F or 2-wire RS-485

  - RS-485 Mode: 9,600 to 115,200 bps, asynchronous, half-duplex, 1 start bit, 8 data bits, and 1 stop bit. Maximum cable length: 2000 ft. (609.6 m)

  - LED Output: TTL levels, high>3 V, low<0.5 V, 5 mA source/sink maximum

  - Buzzer Output: Open collector, 12 Vdc open circuit maximum, 40 mA sink maximum

- Cable requirements

  - Power: 1 twisted pair, 18 AWG

  - RS-485 I/O devices: 1 twisted pair with drain wire and shield, 24 AWG, 120 ohm impedance, 4,000 ft. (1,219 m) max.

  - Alarm Inputs: 1 twisted pair, 30 ohms maximum

  - Outputs: As required for the load

  - Readers:

    - Wiegand (TTL): 6-conductor, 18 AWG, 500 ft. (150 m) maximum

    - F/2F: 4-conductor, 18 AWG, 500 ft. (150 m) maximum

    - OSDP (RS-485): 1 twisted pair with drain wire and shield, 24 AWG, 120 ohm impedance, 2,000 ft. (610 m) maximum

- Environmental

  - Temperature:

    - -55 to +85 °C, storage

    - -40 to +70 °C, operating

  - Humidity: 5 to 95 % RHNC

- Mechanical

  - Dimension: 4.25 in. (108 mm) W x 2.75 in. (70 mm) L x 1 in. (25.4 mm) H

  - Weight: 4 oz. (120 g) nominal, board only

- Product Compliance

  - UL294 Recognized

  - FCC Part 15 Class A

  - CE Compliant

  - RoHS (2011/65/EU & 2015/863)

  - EU REACH (1907/2006)

  - California Proposition 65

- Warranty: Mercury Security warrants the product is free from defects in material and workmanship under normal use and service with proper maintenance for one year from the date of factory shipment.

2.02	Technical Features

- Connectivity: 2-wire RS-485

- Door Control: OSDP (RS-485), Wiegand (Data-1/Data-0), clock/data, two programmable inputs, two relay outputs

- Card Formats:

  - Eight active card formats per intelligent controller

  - 19 digit (64-bit) User ID and 15 digit PIN numbers maximum

  - PIV-II, CAC, TWIC card compatible

- Card Reader Functions

  - Multiple card format support by reader

  - Biometric device support

  - Keypad support with programmable user commands, card input

- Database Functions

  - Supports up to nineteen (19) digital card numbers

  - Supports pin codes up to fifteen (15) digits

- Intrusion Alarm Functions

  - Supports entry delays and exit delays

- Offline mode operation

  - Door mode

    - Unlocked, locked, facility code only

  - Relay Mode

    - Programmable for offline conditions

End of Section