SECTION 28 13 26.06

ACCESS CONTROL REMOTE DEVICES

PART 2 - PRODUCTS

2.01	General

- The family of intelligent controllers and peripheral interface devices must provide an open architecture family of products that enables a choice of host software system vendor without replacement of hardware.

- The peripheral interface device shall control two physical barriers and up to four readers (using OSDP).

- The peripheral interface device shall support a wide range of reader technologies and protocol/electrical signaling standards, including OSDP (RS-485), OSDP SC (RS-485), Wiegand (TTL), magnetic stripe, F/2F and biometric. Wiegand and magnetic strip protocols must support one or two wire LED controls, and buzzer control.

- The reader ports of the peripheral interface device shall be capable of supporting multi-dropped OSDP readers.

- The peripheral interface device shall be able to utilize a cryptographic module that can encrypt/decrypt communication with the intelligent controller, supporting AES encryption using a minimum 256 bit key length.

- The peripheral interface device shall utilize a crypto memory chip that provides hardened protection of secrets such as OSDP secure channel keys.

2.01	Technical Specifications

- The MR52-S3 is for use in low voltage, Class 2 circuits only

- The installation of this device must comply with all local fire and electrical codes.

- Primary Power: 12-24 Volts DC +/- 10%, 550mA maximum (reader current not included)

- Intelligent Controller Communication: 2-wire RS-485 supporting 9600, 19200, 38400 or 115200 bps

- Inputs: Eight unsupervised/supervised, standard EOL: 1k/1k ohm, 1%, ¼ watt, Two unsupervised dedicated for cabinet tamper and UPS fault

- Outputs: Six relays, Form-C with dry contacts Normally open (NO) contact: 5 A @ 30 Vdc resistive, Normally closed (NC) contact: 3 A @ 30 Vdc resistive

- Reader Interface: Two reader ports

  - Power:

    - 12 Vdc ± 10 % regulated, 300 mA maximum each reader (input voltage (VIN) must be greater than 20 Vdc) or

    - 12 to 24 Vdc ± 10 % (input voltage passed through), 300 mA maximum each reader

  - Data Inputs: TTL compatible, F/2F or 2-wire RS-485

  - RS-485 Mode: 9,600 to 115,200 bps, asynchronous, half-duplex, 1 start bit, 8 data bits, and 1 stop bit. Maximum cable length: 2000 ft. (609.6 m)

  - LED Output: TTL levels, high>3 V, low<0.5 V, 5 mA source/sink maximum

  - Buzzer Output: Open collector, 12 Vdc open circuit maximum, 40 mA sink maximum

- Cable requirements

  - Power: 1 twisted pair, 18 AWG

  - RS-485 I/O devices: 1 twisted pair with drain wire and shield, 24 AWG, 120 ohm impedance, 4,000 ft. (1,219 m) max.

  - Alarm Inputs: 1 twisted pair, 30 ohms maximum

  - Outputs: As required for the load

  - Readers:

    - Wiegand (TTL): 6-conductor, 18 AWG, 500 ft. (150 m) maximum

    - F/2F: 4-conductor, 18 AWG, 500 ft. (150 m) maximum

    - OSDP (RS-485): 1 twisted pair with drain wire and shield, 24 AWG, 120 ohm impedance, 2,000 ft. (610 m) maximum

- Environmental

  - Temperature:

    - -55 to +85 °C, storage

    - -0 to +70 °C, operating

  - Humidity: 5 to 95 % RHNC

- Mechanical

  - Dimension: 6 in. (15 2mm) W x 8 in. (203 mm) L x 1 in. (25 mm) H

  - Weight: 11 oz. (312 g) nominal

- Product Compliance

  - UL294 Recognized

  - FCC Part 15 Class A

  - CE Compliant

  - RoHS (2011/65/EU & 2015/863)

  - EU REACH (1907/2006)

  - California Proposition 65

- Warranty: Mercury Security warrants the product is free from defects in material and workmanship under normal use and service with proper maintenance for one year from the date of factory shipment.

2.02	Technical Features

- Card Formats:

  - Eight active card formats per intelligent controller

  - 19 digit (64-bit) User ID and 15 digit PIN numbers maximum

  - PIV-II, CAC, TWIC card compatible

- Card Reader Functions

  - Multiple card format support by reader

  - Paired reader support

  - Alternate reader support

  - Turnstile support

  - Biometric device support

  - Keypad support with programmable user commands, card input

  - Shunt relay support

  - Strike follower relay support

- Database Functions

  - Supports up to nineteen (19) digital card numbers

- Intrusion Alarm Functions

  - Supports entry delays and exit delays

  - Provides control and alarm processing from the keypad

- Offline mode operation

  - Door mode

    - Unlocked, locked, facility code only

  - Relay Mode

    - Programmable for offline conditions

End of Section